## Cover
DVM Pro 2.0
Report
Project
Customer:
|  | Project Name: | Szpital Poznań Pomieszczenia techniczne
|  | Location: | Poland, POZNAN
|  | Date: | 2021-11-25
Designer
|  | Name: | Mateusz Wielk
|  | Phone: | +48 600 099 250
|  | Email: | m.wielk@partner.samsung.com
|  | Address: | Samsung Electronics Polska
Software
|  | Version: | 2.0.0.51
|  | DB version: | 20211123-153906
Table of Abbreviations
| Abbreviation |  |  | Description
| Add. Ref. |  |  | Additional Refrigerant
| AM |  |  | Airflow Mode
| Block Load |  |  | Block Load
| CM |  |  | Cooling Operation Mode
| Corr. Capa |  |  | Correction Capacity
| Corr. PI |  |  | Correction Power Input
| CR |  |  | Combination Ratio
| DB |  |  | Dry Bulb Temperature
| Des Temp |  |  | Design Temperature
| Dis. Temp. |  |  | Discharge Temperature
| Equip. Name |  |  | Equipment Name
| EWT |  |  | Entering Water Temperature
| FR |  |  | Flow Rate
| HM |  |  | Heating Operation Mode
| IDU |  |  | Indoor Unit
| LWT |  |  | Leaving Water Temperature
| Max. Capa |  |  | Maximum Capacity
| Min. HOR |  |  | Minimum Heating Operation Ratio
| ODU |  |  | Outdoor Unit
| Op. WF Range |  |  | Operating Water Flow Range
| Op. WT Range |  |  | Operating Water Temperature Range
| Operating Temp. Range |  |  | Operating Temperature Range
| PHE |  |  | Plate Heat Exchanger
| Pipe Mat. |  |  | Piping Material
| PL |  |  | Pressure Loss
| PWL |  |  | Sound Power level
| Ref. Pipe |  |  | Refrigerant Pipe
| Rq. Vent. Vol. |  |  | Required Ventilation Volume
| SHC |  |  | Sensible Heat Capacity
| SPL |  |  | Sound Pressure Level
| TC |  |  | Total Capacity
| WB |  |  | Wet Bulb Temperature
| 47/43, 120 |  |  | DB / WB, LWT (for DVM Chiller Heating capacity)

## Equipment List
DVM Pro 2.0
Equipment List
Type | Model Code | Qty. | Description
ODU | AC071JXSCEH/EU | 8 | Heat Pump , Low-ambient (Nordic)
| AC100JXSCGH/EU | 2 | Heat Pump , Low-ambient (Nordic)
IDU | AC071KNADEH/EU | 8 | Wall Mounted , AR5000
| AC100MNTCEH/EU | 2 | Wall Mounted , Max
Controller | MWR-WG00KN | 5 | Wired remote controller
| MIM-B14 | 10 | External contact interface
Add. Ref. | R410A | 8.32 | kg
Type | Size | Length [m] / Quantity [EA]
|  | Liquid Pipe |  | Gas Pipe | H.P. Gas | Total
Ref. Pipe | 9.52(3/8'') | 424.96 |  | 0.00 | 0.00 | 424.96
| 15.88(5/8'') | 0.00 |  | 424.96 | 0.00 | 424.96

## Piping System
DVM Pro 2.0
Piping
System (System_RGP_1a)
Design Condition
Design Condition (Air) |  |  |  |  | Outdoor | [11 empty] | Indoor
[5 empty] | CM | [5 empty] | HM | [5 empty] | CM | [5 empty] | HM
Temperature (DB/WB) [°C] |  |  |  |  | 30.0 / 21.0 | [5 empty] | -18.0 / -18.0 | [5 empty] | 25.0 / 18.0 | [5 empty] | 20.0 / 15.0
Load Summary
Floor | Room Name |  |  |  | Area [m²] | [5 empty] | Load [kW]
[11 empty] | CM | [11 empty] | HM
[11 empty] | TC | [5 empty] | SHC | [5 empty] | TC
B1 | -1/014 RGP |  |  |  | 10.98 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Total |  |  |  |  | 10.98 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Installation
Type | Floor |  |  | Room Name | [5 empty] | Equip. Name | [8 empty] | Model Code
ODU | R |  |  | - | [5 empty] | System_RGP_1a | [8 empty] | AC071JXSCEH/EU
IDU | B1 |  |  | -1/014 RGP | [5 empty] | -1/014 RGP_IDU2 | [8 empty] | AC071KNADEH/EU
Outdoor Unit
Equip. Name |  |  | Model Code |  |  |  | CR [%] |  |  |  |  | Max. Capa. [kW] | [7 empty] | Corr. Capa. [kW]
[12 empty] | CM |  |  |  | HM |  |  |  | CM |  |  |  |  | HM
System_RGP_1a |  |  | AC071JXSCEH/EU |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | 7.17 |  |  |  |  | 7.67
Indoor Unit
Equip. Name |  | Model Code |  |  |  | AM |  | Des Temp[°C] | [5 empty] | Max. Capa. [kW] | [6 empty] | Corr. Capa. [kW]
[8 empty] | CM |  |  | HM |  |  | CM |  |  |  | HM |  |  | CM |  |  |  |  | HM
[8 empty] | WB |  |  | DB |  |  | TC |  | SHC |  | TC |  |  | TC |  |  | SHC |  | TC
-1/014 RGP_IDU2 |  | AC071KNADEH/EU |  |  |  | - |  | 18.0 |  |  | 20.0 |  |  | - |  | - |  | - |  |  | 7.17 |  |  | - |  | 7.67
Accessory
Equip. Name |  | Model Code |  |  |  | Address | [6 empty] | Accessory
[6 empty] | Main |  |  | RMC
System_RGP_1a |  | AC071JXSCEH/EU |  |  |  | - | - |  | - |  | -
-1/014 RGP_IDU2 |  | AC071KNADEH/EU |  |  |  | - | - |  | - |  | -
DVM Pro 2.0
Piping (Continued)
System (System_RGP_1a) (Continued)
System Check Result
Checklist | [14 empty] | Restriction Value | [6 empty] | Design Result
Long pipe length is 31.22 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 31.22 m
Total pipe length is 31.22 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 31.22 m
Height difference between ODU and IDU is 19.55 m (restriction: 30.00 m) (ODU higher than IDUs). | [14 empty] | 30.00 m | [6 empty] | 19.55 m
Height difference between ODU and IDU is 0.00 m (restriction: 30.00 m) (ODU lower than IDUs). | [14 empty] | 30.00 m | [6 empty] | 0.00 m
Refrigerant
Factory Charging and Additional Refrigerant Amount | [14 empty] | Refrigerant Amount [kg]
Factory Charging Refrigerant Amount | [14 empty] | 2.90
Additional Refrigerant Amount | [14 empty] | 0.66
Total | [14 empty] | 3.56
DVM Pro 2.0
Piping (Continued)
System (System_RGB_1b)
Design Condition
Design Condition (Air) |  |  |  |  | Outdoor | [11 empty] | Indoor
[5 empty] | CM | [5 empty] | HM | [5 empty] | CM | [5 empty] | HM
Temperature (DB/WB) [°C] |  |  |  |  | 30.0 / 21.0 | [5 empty] | -18.0 / -18.0 | [5 empty] | 25.0 / 18.0 | [5 empty] | 20.0 / 15.0
Load Summary
Floor | Room Name |  |  |  | Area [m²] | [5 empty] | Load [kW]
[11 empty] | CM | [11 empty] | HM
[11 empty] | TC | [5 empty] | SHC | [5 empty] | TC
B1 | -1/014 RGP |  |  |  | 10.98 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Total |  |  |  |  | 10.98 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Installation
Type | Floor |  |  | Room Name | [5 empty] | Equip. Name | [8 empty] | Model Code
ODU | R |  |  | - | [5 empty] | System_RGB_1b | [8 empty] | AC071JXSCEH/EU
IDU | B1 |  |  | -1/014 RGP | [5 empty] | -1/014 RGP_IDU3 | [8 empty] | AC071KNADEH/EU
Outdoor Unit
Equip. Name |  |  | Model Code |  |  |  | CR [%] |  |  |  |  | Max. Capa. [kW] | [7 empty] | Corr. Capa. [kW]
[12 empty] | CM |  |  |  | HM |  |  |  | CM |  |  |  |  | HM
System_RGB_1b |  |  | AC071JXSCEH/EU |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | 7.17 |  |  |  |  | 7.67
Indoor Unit
Equip. Name |  | Model Code |  |  |  | AM |  | Des Temp[°C] | [5 empty] | Max. Capa. [kW] | [6 empty] | Corr. Capa. [kW]
[8 empty] | CM |  |  | HM |  |  | CM |  |  |  | HM |  |  | CM |  |  |  |  | HM
[8 empty] | WB |  |  | DB |  |  | TC |  | SHC |  | TC |  |  | TC |  |  | SHC |  | TC
-1/014 RGP_IDU3 |  | AC071KNADEH/EU |  |  |  | - |  | 18.0 |  |  | 20.0 |  |  | - |  | - |  | - |  |  | 7.17 |  |  | - |  | 7.67
Accessory
Equip. Name |  | Model Code |  |  |  | Address | [6 empty] | Accessory
[6 empty] | Main |  |  | RMC
System_RGB_1b |  | AC071JXSCEH/EU |  |  |  | - | - |  | - |  | -
-1/014 RGP_IDU3 |  | AC071KNADEH/EU |  |  |  | - | - |  | - |  | -
DVM Pro 2.0
Piping (Continued)
System (System_RGB_1b) (Continued)
System Check Result
Checklist | [14 empty] | Restriction Value | [6 empty] | Design Result
Long pipe length is 31.08 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 31.08 m
Total pipe length is 31.08 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 31.08 m
Height difference between ODU and IDU is 19.55 m (restriction: 30.00 m) (ODU higher than IDUs). | [14 empty] | 30.00 m | [6 empty] | 19.55 m
Height difference between ODU and IDU is 0.00 m (restriction: 30.00 m) (ODU lower than IDUs). | [14 empty] | 30.00 m | [6 empty] | 0.00 m
Refrigerant
Factory Charging and Additional Refrigerant Amount | [14 empty] | Refrigerant Amount [kg]
Factory Charging Refrigerant Amount | [14 empty] | 2.90
Additional Refrigerant Amount | [14 empty] | 0.65
Total | [14 empty] | 3.55
DVM Pro 2.0
Piping (Continued)
System (System_RGNN_2b)
Design Condition
Design Condition (Air) |  |  |  |  | Outdoor | [11 empty] | Indoor
[5 empty] | CM | [5 empty] | HM | [5 empty] | CM | [5 empty] | HM
Temperature (DB/WB) [°C] |  |  |  |  | 30.0 / 21.0 | [5 empty] | -18.0 / -18.0 | [5 empty] | 30.0 / 19.0 | [5 empty] | 20.0 / 15.0
Load Summary
Floor | Room Name |  |  |  | Area [m²] | [5 empty] | Load [kW]
[11 empty] | CM | [11 empty] | HM
[11 empty] | TC | [5 empty] | SHC | [5 empty] | TC
B1 | -1/012 RGNN |  |  |  | 54.43 | [5 empty] | - | [5 empty] | 8.00 | [5 empty] | -
Total |  |  |  |  | 54.43 | [5 empty] | - | [5 empty] | 8.00 | [5 empty] | -
Installation
Type | Floor |  |  | Room Name | [5 empty] | Equip. Name | [8 empty] | Model Code
ODU | R |  |  | - | [5 empty] | System_RGNN_2b | [8 empty] | AC100JXSCGH/EU
IDU | B1 |  |  | -1/012 RGNN | [5 empty] | -1/012 RGNN_IDU4 | [8 empty] | AC100MNTCEH/EU
Outdoor Unit
Equip. Name |  |  | Model Code |  |  |  | CR [%] |  |  |  |  | Max. Capa. [kW] | [7 empty] | Corr. Capa. [kW]
[12 empty] | CM |  |  |  | HM |  |  |  | CM |  |  |  |  | HM
System_RGNN_2b |  |  | AC100JXSCGH/EU |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | 9.55 |  |  |  |  | 10.53
Indoor Unit
Equip. Name |  | Model Code |  |  |  | AM |  | Des Temp[°C] | [5 empty] | Max. Capa. [kW] | [6 empty] | Corr. Capa. [kW]
[8 empty] | CM |  |  | HM |  |  | CM |  |  |  | HM |  |  | CM |  |  |  |  | HM
[8 empty] | WB |  |  | DB |  |  | TC |  | SHC |  | TC |  |  | TC |  |  | SHC |  | TC
-1/012 RGNN_IDU4 |  | AC100MNTCEH/EU |  |  |  | - |  | 19.0 |  |  | 20.0 |  |  | - |  | - |  | - |  |  | 9.55 |  |  | - |  | 10.53
Accessory
Equip. Name |  | Model Code |  |  |  | Address | [6 empty] | Accessory
[6 empty] | Main |  |  | RMC
System_RGNN_2b |  | AC100JXSCGH/EU |  |  |  | - | - |  | - |  | -
-1/012 RGNN_IDU4 |  | AC100MNTCEH/EU |  |  |  | - | - |  | - |  | -
DVM Pro 2.0
Piping (Continued)
System (System_RGNN_2b) (Continued)
System Check Result
Checklist | [14 empty] | Restriction Value | [6 empty] | Design Result
Long pipe length is 35.66 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 35.66 m
Total pipe length is 35.66 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 35.66 m
Height difference between ODU and IDU is 19.55 m (restriction: 30.00 m) (ODU higher than IDUs). | [14 empty] | 30.00 m | [6 empty] | 19.55 m
Height difference between ODU and IDU is 0.00 m (restriction: 30.00 m) (ODU lower than IDUs). | [14 empty] | 30.00 m | [6 empty] | 0.00 m
Refrigerant
Factory Charging and Additional Refrigerant Amount | [14 empty] | Refrigerant Amount [kg]
Factory Charging Refrigerant Amount | [14 empty] | 2.90
Additional Refrigerant Amount | [14 empty] | 0.28
Total | [14 empty] | 3.18
DVM Pro 2.0
Piping (Continued)
System (System_RGNN_2a)
Design Condition
Design Condition (Air) |  |  |  |  | Outdoor | [11 empty] | Indoor
[5 empty] | CM | [5 empty] | HM | [5 empty] | CM | [5 empty] | HM
Temperature (DB/WB) [°C] |  |  |  |  | 30.0 / 21.0 | [5 empty] | -18.0 / -18.0 | [5 empty] | 30.0 / 19.0 | [5 empty] | 20.0 / 15.0
Load Summary
Floor | Room Name |  |  |  | Area [m²] | [5 empty] | Load [kW]
[11 empty] | CM | [11 empty] | HM
[11 empty] | TC | [5 empty] | SHC | [5 empty] | TC
B1 | -1/012 RGNN |  |  |  | 54.43 | [5 empty] | - | [5 empty] | 8.00 | [5 empty] | -
Total |  |  |  |  | 54.43 | [5 empty] | - | [5 empty] | 8.00 | [5 empty] | -
Installation
Type | Floor |  |  | Room Name | [5 empty] | Equip. Name | [8 empty] | Model Code
ODU | R |  |  | - | [5 empty] | System_RGNN_2a | [8 empty] | AC100JXSCGH/EU
IDU | B1 |  |  | -1/012 RGNN | [5 empty] | -1/012 RGNN_IDU5 | [8 empty] | AC100MNTCEH/EU
Outdoor Unit
Equip. Name |  |  | Model Code |  |  |  | CR [%] |  |  |  |  | Max. Capa. [kW] | [7 empty] | Corr. Capa. [kW]
[12 empty] | CM |  |  |  | HM |  |  |  | CM |  |  |  |  | HM
System_RGNN_2a |  |  | AC100JXSCGH/EU |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | 9.63 |  |  |  |  | 10.54
Indoor Unit
Equip. Name |  | Model Code |  |  |  | AM |  | Des Temp[°C] | [5 empty] | Max. Capa. [kW] | [6 empty] | Corr. Capa. [kW]
[8 empty] | CM |  |  | HM |  |  | CM |  |  |  | HM |  |  | CM |  |  |  |  | HM
[8 empty] | WB |  |  | DB |  |  | TC |  | SHC |  | TC |  |  | TC |  |  | SHC |  | TC
-1/012 RGNN_IDU5 |  | AC100MNTCEH/EU |  |  |  | - |  | 19.0 |  |  | 20.0 |  |  | - |  | - |  | - |  |  | 9.63 |  |  | - |  | 10.54
Accessory
Equip. Name |  | Model Code |  |  |  | Address | [6 empty] | Accessory
[6 empty] | Main |  |  | RMC
System_RGNN_2a |  | AC100JXSCGH/EU |  |  |  | - | - |  | - |  | -
-1/012 RGNN_IDU5 |  | AC100MNTCEH/EU |  |  |  | - | - |  | - |  | -
DVM Pro 2.0
Piping (Continued)
System (System_RGNN_2a) (Continued)
System Check Result
Checklist | [14 empty] | Restriction Value | [6 empty] | Design Result
Long pipe length is 32.08 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 32.08 m
Total pipe length is 32.08 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 32.08 m
Height difference between ODU and IDU is 19.55 m (restriction: 30.00 m) (ODU higher than IDUs). | [14 empty] | 30.00 m | [6 empty] | 19.55 m
Height difference between ODU and IDU is 0.00 m (restriction: 30.00 m) (ODU lower than IDUs). | [14 empty] | 30.00 m | [6 empty] | 0.00 m
Refrigerant
Factory Charging and Additional Refrigerant Amount | [14 empty] | Refrigerant Amount [kg]
Factory Charging Refrigerant Amount | [14 empty] | 2.90
Additional Refrigerant Amount | [14 empty] | 0.10
Total | [14 empty] | 3.00
DVM Pro 2.0
Piping (Continued)
System (System_UPS_3a)
Design Condition
Design Condition (Air) |  |  |  |  | Outdoor | [11 empty] | Indoor
[5 empty] | CM | [5 empty] | HM | [5 empty] | CM | [5 empty] | HM
Temperature (DB/WB) [°C] |  |  |  |  | 30.0 / 21.0 | [5 empty] | -18.0 / -18.0 | [5 empty] | 25.0 / 18.0 | [5 empty] | 20.0 / 15.0
Load Summary
Floor | Room Name |  |  |  | Area [m²] | [5 empty] | Load [kW]
[11 empty] | CM | [11 empty] | HM
[11 empty] | TC | [5 empty] | SHC | [5 empty] | TC
B1 | -1/017 UPS |  |  |  | 15.18 | [5 empty] | - | [5 empty] | 4.00 | [5 empty] | -
Total |  |  |  |  | 15.18 | [5 empty] | - | [5 empty] | 4.00 | [5 empty] | -
Installation
Type | Floor |  |  | Room Name | [5 empty] | Equip. Name | [8 empty] | Model Code
ODU | R |  |  | - | [5 empty] | System_UPS_3a | [8 empty] | AC071JXSCEH/EU
IDU | B1 |  |  | -1/017 UPS | [5 empty] | -1/017 UPS_IDU6 | [8 empty] | AC071KNADEH/EU
Outdoor Unit
Equip. Name |  |  | Model Code |  |  |  | CR [%] |  |  |  |  | Max. Capa. [kW] | [7 empty] | Corr. Capa. [kW]
[12 empty] | CM |  |  |  | HM |  |  |  | CM |  |  |  |  | HM
System_UPS_3a |  |  | AC071JXSCEH/EU |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | 7.90 |  |  |  |  | 7.67
Indoor Unit
Equip. Name |  | Model Code |  |  |  | AM |  | Des Temp[°C] | [5 empty] | Max. Capa. [kW] | [6 empty] | Corr. Capa. [kW]
[8 empty] | CM |  |  | HM |  |  | CM |  |  |  | HM |  |  | CM |  |  |  |  | HM
[8 empty] | WB |  |  | DB |  |  | TC |  | SHC |  | TC |  |  | TC |  |  | SHC |  | TC
-1/017 UPS_IDU6 |  | AC071KNADEH/EU |  |  |  | - |  | 22.0 |  |  | 20.0 |  |  | - |  | - |  | - |  |  | 7.90 |  |  | - |  | 7.67
Accessory
Equip. Name |  | Model Code |  |  |  | Address | [6 empty] | Accessory
[6 empty] | Main |  |  | RMC
System_UPS_3a |  | AC071JXSCEH/EU |  |  |  | - | - |  | - |  | -
-1/017 UPS_IDU6 |  | AC071KNADEH/EU |  |  |  | - | - |  | - |  | -
DVM Pro 2.0
Piping (Continued)
System (System_UPS_3a) (Continued)
System Check Result
Checklist | [14 empty] | Restriction Value | [6 empty] | Design Result
Long pipe length is 35.18 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 35.18 m
Total pipe length is 35.18 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 35.18 m
Height difference between ODU and IDU is 19.55 m (restriction: 30.00 m) (ODU higher than IDUs). | [14 empty] | 30.00 m | [6 empty] | 19.55 m
Height difference between ODU and IDU is 0.00 m (restriction: 30.00 m) (ODU lower than IDUs). | [14 empty] | 30.00 m | [6 empty] | 0.00 m
Refrigerant
Factory Charging and Additional Refrigerant Amount | [14 empty] | Refrigerant Amount [kg]
Factory Charging Refrigerant Amount | [14 empty] | 2.90
Additional Refrigerant Amount | [14 empty] | 0.75
Total | [14 empty] | 3.65
DVM Pro 2.0
Piping (Continued)
System (System_UPS_3b)
Design Condition
Design Condition (Air) |  |  |  |  | Outdoor | [11 empty] | Indoor
[5 empty] | CM | [5 empty] | HM | [5 empty] | CM | [5 empty] | HM
Temperature (DB/WB) [°C] |  |  |  |  | 30.0 / 21.0 | [5 empty] | -18.0 / -18.0 | [5 empty] | 25.0 / 18.0 | [5 empty] | 20.0 / 15.0
Load Summary
Floor | Room Name |  |  |  | Area [m²] | [5 empty] | Load [kW]
[11 empty] | CM | [11 empty] | HM
[11 empty] | TC | [5 empty] | SHC | [5 empty] | TC
B1 | -1/017 UPS |  |  |  | 15.18 | [5 empty] | - | [5 empty] | 4.00 | [5 empty] | -
Total |  |  |  |  | 15.18 | [5 empty] | - | [5 empty] | 4.00 | [5 empty] | -
Installation
Type | Floor |  |  | Room Name | [5 empty] | Equip. Name | [8 empty] | Model Code
ODU | R |  |  | - | [5 empty] | System_UPS_3b | [8 empty] | AC071JXSCEH/EU
IDU | B1 |  |  | -1/017 UPS | [5 empty] | -1/017 UPS_IDU7 | [8 empty] | AC071KNADEH/EU
Outdoor Unit
Equip. Name |  |  | Model Code |  |  |  | CR [%] |  |  |  |  | Max. Capa. [kW] | [7 empty] | Corr. Capa. [kW]
[12 empty] | CM |  |  |  | HM |  |  |  | CM |  |  |  |  | HM
System_UPS_3b |  |  | AC071JXSCEH/EU |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | 7.85 |  |  |  |  | 7.63
Indoor Unit
Equip. Name |  | Model Code |  |  |  | AM |  | Des Temp[°C] | [5 empty] | Max. Capa. [kW] | [6 empty] | Corr. Capa. [kW]
[8 empty] | CM |  |  | HM |  |  | CM |  |  |  | HM |  |  | CM |  |  |  |  | HM
[8 empty] | WB |  |  | DB |  |  | TC |  | SHC |  | TC |  |  | TC |  |  | SHC |  | TC
-1/017 UPS_IDU7 |  | AC071KNADEH/EU |  |  |  | - |  | 22.0 |  |  | 20.0 |  |  | - |  | - |  | - |  |  | 7.85 |  |  | - |  | 7.63
Accessory
Equip. Name |  | Model Code |  |  |  | Address | [6 empty] | Accessory
[6 empty] | Main |  |  | RMC
System_UPS_3b |  | AC071JXSCEH/EU |  |  |  | - | - |  | - |  | -
-1/017 UPS_IDU7 |  | AC071KNADEH/EU |  |  |  | - | - |  | - |  | -
DVM Pro 2.0
Piping (Continued)
System (System_UPS_3b) (Continued)
System Check Result
Checklist | [14 empty] | Restriction Value | [6 empty] | Design Result
Long pipe length is 37.80 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 37.80 m
Total pipe length is 37.80 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 37.80 m
Height difference between ODU and IDU is 19.55 m (restriction: 30.00 m) (ODU higher than IDUs). | [14 empty] | 30.00 m | [6 empty] | 19.55 m
Height difference between ODU and IDU is 0.00 m (restriction: 30.00 m) (ODU lower than IDUs). | [14 empty] | 30.00 m | [6 empty] | 0.00 m
Refrigerant
Factory Charging and Additional Refrigerant Amount | [14 empty] | Refrigerant Amount [kg]
Factory Charging Refrigerant Amount | [14 empty] | 2.90
Additional Refrigerant Amount | [14 empty] | 0.82
Total | [14 empty] | 3.72
DVM Pro 2.0
Piping (Continued)
System (System_PSP_4a)
Design Condition
Design Condition (Air) |  |  |  |  | Outdoor | [11 empty] | Indoor
[5 empty] | CM | [5 empty] | HM | [5 empty] | CM | [5 empty] | HM
Temperature (DB/WB) [°C] |  |  |  |  | 30.0 / 21.0 | [5 empty] | -18.0 / -18.0 | [5 empty] | 25.0 / 18.0 | [5 empty] | 20.0 / 15.0
Load Summary
Floor | Room Name |  |  |  | Area [m²] | [5 empty] | Load [kW]
[11 empty] | CM | [11 empty] | HM
[11 empty] | TC | [5 empty] | SHC | [5 empty] | TC
B1 | -1/018 Pom systemów poż. |  |  |  | 13.72 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Total |  |  |  |  | 13.72 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Installation
Type | Floor |  |  | Room Name | [5 empty] | Equip. Name | [8 empty] | Model Code
ODU | R |  |  | - | [5 empty] | System_PSP_4a | [8 empty] | AC071JXSCEH/EU
IDU | B1 |  |  | -1/018 Pom systemów poż. | [5 empty] | -1/018 Pom systemów poż._IDU8 | [8 empty] | AC071KNADEH/EU
Outdoor Unit
Equip. Name |  |  | Model Code |  |  |  | CR [%] |  |  |  |  | Max. Capa. [kW] | [7 empty] | Corr. Capa. [kW]
[12 empty] | CM |  |  |  | HM |  |  |  | CM |  |  |  |  | HM
System_PSP_4a |  |  | AC071JXSCEH/EU |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | 7.65 |  |  |  |  | 7.47
Indoor Unit
Equip. Name |  | Model Code |  |  |  | AM |  | Des Temp[°C] | [5 empty] | Max. Capa. [kW] | [6 empty] | Corr. Capa. [kW]
[8 empty] | CM |  |  | HM |  |  | CM |  |  |  | HM |  |  | CM |  |  |  |  | HM
[8 empty] | WB |  |  | DB |  |  | TC |  | SHC |  | TC |  |  | TC |  |  | SHC |  | TC
-1/018 Pom systemów poż._IDU8 |  | AC071KNADEH/EU |  |  |  | - |  | 22.0 |  |  | 20.0 |  |  | - |  | - |  | - |  |  | 7.65 |  |  | - |  | 7.47
Accessory
Equip. Name |  | Model Code |  |  |  | Address | [6 empty] | Accessory
[6 empty] | Main |  |  | RMC
System_PSP_4a |  | AC071JXSCEH/EU |  |  |  | - | - |  | - |  | -
-1/018 Pom systemów poż._IDU8 |  | AC071KNADEH/EU |  |  |  | - | - |  | - |  | -
DVM Pro 2.0
Piping (Continued)
System (System_PSP_4a) (Continued)
System Check Result
Checklist | [14 empty] | Restriction Value | [6 empty] | Design Result
Long pipe length is 52.55 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 52.55 m
Total pipe length is 52.55 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 52.55 m
Height difference between ODU and IDU is 19.55 m (restriction: 30.00 m) (ODU higher than IDUs). | [14 empty] | 30.00 m | [6 empty] | 19.55 m
Height difference between ODU and IDU is 0.00 m (restriction: 30.00 m) (ODU lower than IDUs). | [14 empty] | 30.00 m | [6 empty] | 0.00 m
Refrigerant
Factory Charging and Additional Refrigerant Amount | [14 empty] | Refrigerant Amount [kg]
Factory Charging Refrigerant Amount | [14 empty] | 2.90
Additional Refrigerant Amount | [14 empty] | 1.19
Total | [14 empty] | 4.09
DVM Pro 2.0
Piping (Continued)
System (System_PSP_4b)
Design Condition
Design Condition (Air) |  |  |  |  | Outdoor | [11 empty] | Indoor
[5 empty] | CM | [5 empty] | HM | [5 empty] | CM | [5 empty] | HM
Temperature (DB/WB) [°C] |  |  |  |  | 30.0 / 21.0 | [5 empty] | -18.0 / -18.0 | [5 empty] | 25.0 / 18.0 | [5 empty] | 20.0 / 15.0
Load Summary
Floor | Room Name |  |  |  | Area [m²] | [5 empty] | Load [kW]
[11 empty] | CM | [11 empty] | HM
[11 empty] | TC | [5 empty] | SHC | [5 empty] | TC
B1 | -1/018 Pom systemów poż. |  |  |  | 13.72 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Total |  |  |  |  | 13.72 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Installation
Type | Floor |  |  | Room Name | [5 empty] | Equip. Name | [8 empty] | Model Code
ODU | R |  |  | - | [5 empty] | System_PSP_4b | [8 empty] | AC071JXSCEH/EU
IDU | B1 |  |  | -1/018 Pom systemów poż. | [5 empty] | -1/018 Pom systemów poż._IDU9 | [8 empty] | AC071KNADEH/EU
Outdoor Unit
Equip. Name |  |  | Model Code |  |  |  | CR [%] |  |  |  |  | Max. Capa. [kW] | [7 empty] | Corr. Capa. [kW]
[12 empty] | CM |  |  |  | HM |  |  |  | CM |  |  |  |  | HM
System_PSP_4b |  |  | AC071JXSCEH/EU |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | 7.65 |  |  |  |  | 7.46
Indoor Unit
Equip. Name |  | Model Code |  |  |  | AM |  | Des Temp[°C] | [5 empty] | Max. Capa. [kW] | [6 empty] | Corr. Capa. [kW]
[8 empty] | CM |  |  | HM |  |  | CM |  |  |  | HM |  |  | CM |  |  |  |  | HM
[8 empty] | WB |  |  | DB |  |  | TC |  | SHC |  | TC |  |  | TC |  |  | SHC |  | TC
-1/018 Pom systemów poż._IDU9 |  | AC071KNADEH/EU |  |  |  | - |  | 22.0 |  |  | 20.0 |  |  | - |  | - |  | - |  |  | 7.65 |  |  | - |  | 7.46
Accessory
Equip. Name |  | Model Code |  |  |  | Address | [6 empty] | Accessory
[6 empty] | Main |  |  | RMC
System_PSP_4b |  | AC071JXSCEH/EU |  |  |  | - | - |  | - |  | -
-1/018 Pom systemów poż._IDU9 |  | AC071KNADEH/EU |  |  |  | - | - |  | - |  | -
DVM Pro 2.0
Piping (Continued)
System (System_PSP_4b) (Continued)
System Check Result
Checklist | [14 empty] | Restriction Value | [6 empty] | Design Result
Long pipe length is 53.13 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 53.13 m
Total pipe length is 53.13 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 53.13 m
Height difference between ODU and IDU is 19.55 m (restriction: 30.00 m) (ODU higher than IDUs). | [14 empty] | 30.00 m | [6 empty] | 19.55 m
Height difference between ODU and IDU is 0.00 m (restriction: 30.00 m) (ODU lower than IDUs). | [14 empty] | 30.00 m | [6 empty] | 0.00 m
Refrigerant
Factory Charging and Additional Refrigerant Amount | [14 empty] | Refrigerant Amount [kg]
Factory Charging Refrigerant Amount | [14 empty] | 2.90
Additional Refrigerant Amount | [14 empty] | 1.20
Total | [14 empty] | 4.10
DVM Pro 2.0
Piping (Continued)
System (System_SERW_5a)
Design Condition
Design Condition (Air) |  |  |  |  | Outdoor | [11 empty] | Indoor
[5 empty] | CM | [5 empty] | HM | [5 empty] | CM | [5 empty] | HM
Temperature (DB/WB) [°C] |  |  |  |  | 30.0 / 21.0 | [5 empty] | -18.0 / -18.0 | [5 empty] | 25.0 / 18.0 | [5 empty] | 20.0 / 15.0
Load Summary
Floor | Room Name |  |  |  | Area [m²] | [5 empty] | Load [kW]
[11 empty] | CM | [11 empty] | HM
[11 empty] | TC | [5 empty] | SHC | [5 empty] | TC
B1 | -1/019 Serwerownia |  |  |  | 12.62 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Total |  |  |  |  | 12.62 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Installation
Type | Floor |  |  | Room Name | [5 empty] | Equip. Name | [8 empty] | Model Code
ODU | R |  |  | - | [5 empty] | System_SERW_5a | [8 empty] | AC071JXSCEH/EU
IDU | B1 |  |  | -1/019 Serwerownia | [5 empty] | -1/019 Serwerownia_IDU10 | [8 empty] | AC071KNADEH/EU
Outdoor Unit
Equip. Name |  |  | Model Code |  |  |  | CR [%] |  |  |  |  | Max. Capa. [kW] | [7 empty] | Corr. Capa. [kW]
[12 empty] | CM |  |  |  | HM |  |  |  | CM |  |  |  |  | HM
System_SERW_5a |  |  | AC071JXSCEH/EU |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | 7.55 |  |  |  |  | 7.38
Indoor Unit
Equip. Name |  | Model Code |  |  |  | AM |  | Des Temp[°C] | [5 empty] | Max. Capa. [kW] | [6 empty] | Corr. Capa. [kW]
[8 empty] | CM |  |  | HM |  |  | CM |  |  |  | HM |  |  | CM |  |  |  |  | HM
[8 empty] | WB |  |  | DB |  |  | TC |  | SHC |  | TC |  |  | TC |  |  | SHC |  | TC
-1/019 Serwerownia_IDU10 |  | AC071KNADEH/EU |  |  |  | - |  | 22.0 |  |  | 20.0 |  |  | - |  | - |  | - |  |  | 7.55 |  |  | - |  | 7.38
Accessory
Equip. Name |  | Model Code |  |  |  | Address | [6 empty] | Accessory
[6 empty] | Main |  |  | RMC
System_SERW_5a |  | AC071JXSCEH/EU |  |  |  | - | - |  | - |  | -
-1/019 Serwerownia_IDU10 |  | AC071KNADEH/EU |  |  |  | - | - |  | - |  | -
DVM Pro 2.0
Piping (Continued)
System (System_SERW_5a) (Continued)
System Check Result
Checklist | [14 empty] | Restriction Value | [6 empty] | Design Result
Long pipe length is 58.22 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 58.22 m
Total pipe length is 58.22 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 58.22 m
Height difference between ODU and IDU is 19.55 m (restriction: 30.00 m) (ODU higher than IDUs). | [14 empty] | 30.00 m | [6 empty] | 19.55 m
Height difference between ODU and IDU is 0.00 m (restriction: 30.00 m) (ODU lower than IDUs). | [14 empty] | 30.00 m | [6 empty] | 0.00 m
Refrigerant
Factory Charging and Additional Refrigerant Amount | [14 empty] | Refrigerant Amount [kg]
Factory Charging Refrigerant Amount | [14 empty] | 2.90
Additional Refrigerant Amount | [14 empty] | 1.33
Total | [14 empty] | 4.23
DVM Pro 2.0
Piping (Continued)
System (System_SERW_5b)
Design Condition
Design Condition (Air) |  |  |  |  | Outdoor | [11 empty] | Indoor
[5 empty] | CM | [5 empty] | HM | [5 empty] | CM | [5 empty] | HM
Temperature (DB/WB) [°C] |  |  |  |  | 30.0 / 21.0 | [5 empty] | -18.0 / -18.0 | [5 empty] | 25.0 / 18.0 | [5 empty] | 20.0 / 15.0
Load Summary
Floor | Room Name |  |  |  | Area [m²] | [5 empty] | Load [kW]
[11 empty] | CM | [11 empty] | HM
[11 empty] | TC | [5 empty] | SHC | [5 empty] | TC
B1 | -1/019 Serwerownia |  |  |  | 12.62 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Total |  |  |  |  | 12.62 | [5 empty] | - | [5 empty] | 2.00 | [5 empty] | -
Installation
Type | Floor |  |  | Room Name | [5 empty] | Equip. Name | [8 empty] | Model Code
ODU | R |  |  | - | [5 empty] | System_SERW_5b | [8 empty] | AC071JXSCEH/EU
IDU | B1 |  |  | -1/019 Serwerownia | [5 empty] | -1/019 Serwerownia_IDU11 | [8 empty] | AC071KNADEH/EU
Outdoor Unit
Equip. Name |  |  | Model Code |  |  |  | CR [%] |  |  |  |  | Max. Capa. [kW] | [7 empty] | Corr. Capa. [kW]
[12 empty] | CM |  |  |  | HM |  |  |  | CM |  |  |  |  | HM
System_SERW_5b |  |  | AC071JXSCEH/EU |  |  |  | - |  |  |  |  | - |  |  |  | - |  |  |  | 7.55 |  |  |  |  | 7.38
Indoor Unit
Equip. Name |  | Model Code |  |  |  | AM |  | Des Temp[°C] | [5 empty] | Max. Capa. [kW] | [6 empty] | Corr. Capa. [kW]
[8 empty] | CM |  |  | HM |  |  | CM |  |  |  | HM |  |  | CM |  |  |  |  | HM
[8 empty] | WB |  |  | DB |  |  | TC |  | SHC |  | TC |  |  | TC |  |  | SHC |  | TC
-1/019 Serwerownia_IDU11 |  | AC071KNADEH/EU |  |  |  | - |  | 22.0 |  |  | 20.0 |  |  | - |  | - |  | - |  |  | 7.55 |  |  | - |  | 7.38
Accessory
Equip. Name |  | Model Code |  |  |  | Address | [6 empty] | Accessory
[6 empty] | Main |  |  | RMC
System_SERW_5b |  | AC071JXSCEH/EU |  |  |  | - | - |  | - |  | -
-1/019 Serwerownia_IDU11 |  | AC071KNADEH/EU |  |  |  | - | - |  | - |  | -
DVM Pro 2.0
Piping (Continued)
System (System_SERW_5b) (Continued)
System Check Result
Checklist | [14 empty] | Restriction Value | [6 empty] | Design Result
Long pipe length is 58.04 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 58.04 m
Total pipe length is 58.04 m (Restriction: 75.00 m). | [14 empty] | 75.00 m | [6 empty] | 58.04 m
Height difference between ODU and IDU is 19.55 m (restriction: 30.00 m) (ODU higher than IDUs). | [14 empty] | 30.00 m | [6 empty] | 19.55 m
Height difference between ODU and IDU is 0.00 m (restriction: 30.00 m) (ODU lower than IDUs). | [14 empty] | 30.00 m | [6 empty] | 0.00 m
Refrigerant
Factory Charging and Additional Refrigerant Amount | [14 empty] | Refrigerant Amount [kg]
Factory Charging Refrigerant Amount | [14 empty] | 2.90
Additional Refrigerant Amount | [14 empty] | 1.33
Total | [14 empty] | 4.23

## Specification
DVM Pro 2.0
Product Specification
System_RGP_1a
System
Model Name |  |  |  |  | AC071JXSCEH/EU+AC071KNADEH/EU
Mode |  |  |  |  | HP
Performance | kW |  |  |  | 7.1
| Capacity | Cooling | Standard | kW | 7.10
|  |  | Max | kW | 8.50
|  |  | Min | kW | 2.00
|  | Heating | Standard | kW | 8.00
|  |  | Max | kW | 10.00
|  |  | Min | kW | 3.00
Power | Power Input | Cooling | Standard | kW | 1.86
|  |  | Max | kW | 2.30
|  |  | Min | kW | 0.75
|  | Heating | Standard | kW | 2.33
|  |  | Max | kW | 5.10
|  |  | Min | kW | 0.56
| Current Input | Cooling | Standard | A | 8.40
|  |  | Max | A | 10.30
|  |  | Min | A | 4.10
|  | Heating | Standard | A | 10.60
|  |  | Max | A | 22.00
|  |  | Min | A | 3.00
| Current | MCA |  | A | 25.00
|  | MFA |  | A | 30.00
Efficiency | Cooling | EER |  | W/W | 3.81720430107527
|  | SEER |  | W/W | 6.5
|  | SEER_Class |  | W/W | A++
| Heating | COP |  | W/W | 3.43347639484979
|  | SCOP |  | W/W | 4
|  | SCOP_Class |  | W/W | A+
Piping Connections | Liquid Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 9.52
| Gas Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 15.88
Wiring connections | Communication | Min. |  | ㎟ | 0.75
DVM Pro 2.0
Product Specification
System_RGP_1a (Continued)
System
Wiring connections | Communication | Comm.Layer |  |  | F1, F2
Refrigerant | Type |  |  |  | R410A
| Factory Charging |  |  | kg | 2.90
Operating Temp. Range | Cooling | Min. |  | °C | -20.0
|  | Max. |  | °C | 50.0
| Heating | Min. |  | °C | -25.0
|  | Max. |  | °C | 24.0
DVM Pro 2.0
Product Specification
System_RGP_1a (Continued)
Outdoor Unit
Model Name |  |  |  |  | AC071JXSCEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Casing | Material | Body |  |  | EGI Steel Plate
|  | Base |  |  | EGI Steel Plate
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Compressor | Model Name |  |  |  | UG5T450FUEJX
| Quantity |  |  | EA | 1
| Type |  |  |  | Twin BLDC Inverter Rotary
| Output |  |  | kW | 4.12
| Oil | Type |  |  | POE
|  | Initial charge |  | cc | 1700
Fan | Type |  |  |  | Propeller
| Discharge direction |  |  |  | Horizontal
| Air Flow Rate | High |  | CMM | 112
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
Sound | Sound Pressure Level | Cooling |  | dB(A) | 49
|  | Heating |  | dB(A) | 49
| Sound Power Level | Cooling |  | dB(A) | 65
External Dimension | Net Weight |  |  | kg | 96.00
| Shipping Weight |  |  | kg | 106.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_RGP_1a (Continued)
Indoor Unit
Model Name |  |  |  |  | AC071KNADEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Fan | Type |  |  |  | Cross flow
| Air Flow Rate | High |  | CMM | 17
|  | Mid |  | CMM | 15
|  | Low |  | CMM | 13
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
| Output |  |  | W | 27
Sound | Sound Pressure Level | High |  | dB(A) | 43
|  | Mid |  | dB(A) | 40
|  | Low |  | dB(A) | 35
|  | Silent |  | dB(A) | 30
| Sound Power Level | Cooling |  | dB(A) | 61
External Dimension | Net Weight |  |  | kg | 14.50
| Shipping Weight |  |  | kg | 17.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_RGB_1b
System
Model Name |  |  |  |  | AC071JXSCEH/EU+AC071KNADEH/EU
Mode |  |  |  |  | HP
Performance | kW |  |  |  | 7.1
| Capacity | Cooling | Standard | kW | 7.10
|  |  | Max | kW | 8.50
|  |  | Min | kW | 2.00
|  | Heating | Standard | kW | 8.00
|  |  | Max | kW | 10.00
|  |  | Min | kW | 3.00
Power | Power Input | Cooling | Standard | kW | 1.86
|  |  | Max | kW | 2.30
|  |  | Min | kW | 0.75
|  | Heating | Standard | kW | 2.33
|  |  | Max | kW | 5.10
|  |  | Min | kW | 0.56
| Current Input | Cooling | Standard | A | 8.40
|  |  | Max | A | 10.30
|  |  | Min | A | 4.10
|  | Heating | Standard | A | 10.60
|  |  | Max | A | 22.00
|  |  | Min | A | 3.00
| Current | MCA |  | A | 25.00
|  | MFA |  | A | 30.00
Efficiency | Cooling | EER |  | W/W | 3.81720430107527
|  | SEER |  | W/W | 6.5
|  | SEER_Class |  | W/W | A++
| Heating | COP |  | W/W | 3.43347639484979
|  | SCOP |  | W/W | 4
|  | SCOP_Class |  | W/W | A+
Piping Connections | Liquid Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 9.52
| Gas Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 15.88
Wiring connections | Communication | Min. |  | ㎟ | 0.75
DVM Pro 2.0
Product Specification
System_RGB_1b (Continued)
System
Wiring connections | Communication | Comm.Layer |  |  | F1, F2
Refrigerant | Type |  |  |  | R410A
| Factory Charging |  |  | kg | 2.90
Operating Temp. Range | Cooling | Min. |  | °C | -20.0
|  | Max. |  | °C | 50.0
| Heating | Min. |  | °C | -25.0
|  | Max. |  | °C | 24.0
DVM Pro 2.0
Product Specification
System_RGB_1b (Continued)
Outdoor Unit
Model Name |  |  |  |  | AC071JXSCEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Casing | Material | Body |  |  | EGI Steel Plate
|  | Base |  |  | EGI Steel Plate
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Compressor | Model Name |  |  |  | UG5T450FUEJX
| Quantity |  |  | EA | 1
| Type |  |  |  | Twin BLDC Inverter Rotary
| Output |  |  | kW | 4.12
| Oil | Type |  |  | POE
|  | Initial charge |  | cc | 1700
Fan | Type |  |  |  | Propeller
| Discharge direction |  |  |  | Horizontal
| Air Flow Rate | High |  | CMM | 112
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
Sound | Sound Pressure Level | Cooling |  | dB(A) | 49
|  | Heating |  | dB(A) | 49
| Sound Power Level | Cooling |  | dB(A) | 65
External Dimension | Net Weight |  |  | kg | 96.00
| Shipping Weight |  |  | kg | 106.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_RGB_1b (Continued)
Indoor Unit
Model Name |  |  |  |  | AC071KNADEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Fan | Type |  |  |  | Cross flow
| Air Flow Rate | High |  | CMM | 17
|  | Mid |  | CMM | 15
|  | Low |  | CMM | 13
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
| Output |  |  | W | 27
Sound | Sound Pressure Level | High |  | dB(A) | 43
|  | Mid |  | dB(A) | 40
|  | Low |  | dB(A) | 35
|  | Silent |  | dB(A) | 30
| Sound Power Level | Cooling |  | dB(A) | 61
External Dimension | Net Weight |  |  | kg | 14.50
| Shipping Weight |  |  | kg | 17.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_RGNN_2b
System
Model Name |  |  |  |  | AC100JXSCGH/EU+AC100MNTCEH/EU
Mode |  |  |  |  | HP
Performance | kW |  |  |  | 10
| Capacity | Cooling | Standard | kW | 10.00
|  |  | Max | kW | 12.00
|  |  | Min | kW | 3.50
|  | Heating | Standard | kW | 11.20
|  |  | Max | kW | 17.00
|  |  | Min | kW | 3.30
Power | Power Input | Cooling | Standard | kW | 3.45
|  |  | Max | kW | 4.20
|  |  | Min | kW | 0.85
|  | Heating | Standard | kW | 3.64
|  |  | Max | kW | 6.90
|  |  | Min | kW | 0.72
| Current Input | Cooling | Standard | A | 5.30
|  |  | Max | A | 6.40
|  |  | Min | A | 1.40
|  | Heating | Standard | A | 5.60
|  |  | Max | A | 11.00
|  |  | Min | A | 1.30
| Current | MCA |  | A | 13.10
|  | MFA |  | A | 15.00
Efficiency | Cooling | EER |  | W/W | 2.9
|  | SEER |  | W/W | 6
|  | SEER_Class |  | W/W | A+
| Heating | COP |  | W/W | 3.08
|  | SCOP |  | W/W | 4
|  | SCOP_Class |  | W/W | A+
Piping Connections | Liquid Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 9.52
| Gas Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 15.88
Wiring connections | Communication | Min. |  | ㎟ | 0.75
DVM Pro 2.0
Product Specification
System_RGNN_2b (Continued)
System
Wiring connections | Communication | Comm.Layer |  |  | F1, F2
Refrigerant | Type |  |  |  | R410A
| Factory Charging |  |  | kg | 2.90
Operating Temp. Range | Cooling | Min. |  | °C | -20.0
|  | Max. |  | °C | 50.0
| Heating | Min. |  | °C | -25.0
|  | Max. |  | °C | 24.0
DVM Pro 2.0
Product Specification
System_RGNN_2b (Continued)
Outdoor Unit
Model Name |  |  |  |  | AC100JXSCGH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 3 ¦ 4 ¦ 380-415 ¦ 50
Casing | Material | Body |  |  | EGI Steel Plate
|  | Base |  |  | EGI Steel Plate
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Compressor | Model Name |  |  |  | UG5T450FXAJX
| Quantity |  |  | EA | 1
| Type |  |  |  | Twin BLDC Inverter Rotary
| Output |  |  | kW | 4.01
| Oil | Type |  |  | POE
|  | Initial charge |  | cc | 1700
Fan | Type |  |  |  | Propeller
| Discharge direction |  |  |  | Horizontal
| Air Flow Rate | High |  | CMM | 112
Fan Motor | Type |  |  |  | BLDC
Sound | Sound Pressure Level | Cooling |  | dB(A) | 50
|  | Heating |  | dB(A) | 50
| Sound Power Level | Cooling |  | dB(A) | 66
External Dimension | Net Weight |  |  | kg | 96.00
| Shipping Weight |  |  | kg | 106.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_RGNN_2b (Continued)
Indoor Unit
Model Name |  |  |  |  | AC100MNTCEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
| Fin Treatment |  |  |  | Green Hydrophile
Fan | Type |  |  |  | Crossflow
| Air Flow Rate | High |  | CMM | 24
|  | Mid |  | CMM | 22
|  | Low |  | CMM | 19
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
| Output |  |  | W | 58
Sound | Sound Pressure Level | High |  | dB(A) | 0
|  | Mid |  | dB(A) | 49
|  | Low |  | dB(A) | 0
| Sound Power Level | Cooling |  | dB(A) | 65
External Dimension | Net Weight |  |  | kg | 18.50
| Shipping Weight |  |  | kg | 21.50
| Net Dimensions | W |  | mm | 1280
|  | H |  | mm | 253
|  | D |  | mm | 345
| Shipping Dimensions | W |  | mm | 1352
|  | H |  | mm | 326
|  | D |  | mm | 420
DVM Pro 2.0
Product Specification
System_RGNN_2a
System
Model Name |  |  |  |  | AC100JXSCGH/EU+AC100MNTCEH/EU
Mode |  |  |  |  | HP
Performance | kW |  |  |  | 10
| Capacity | Cooling | Standard | kW | 10.00
|  |  | Max | kW | 12.00
|  |  | Min | kW | 3.50
|  | Heating | Standard | kW | 11.20
|  |  | Max | kW | 17.00
|  |  | Min | kW | 3.30
Power | Power Input | Cooling | Standard | kW | 3.45
|  |  | Max | kW | 4.20
|  |  | Min | kW | 0.85
|  | Heating | Standard | kW | 3.64
|  |  | Max | kW | 6.90
|  |  | Min | kW | 0.72
| Current Input | Cooling | Standard | A | 5.30
|  |  | Max | A | 6.40
|  |  | Min | A | 1.40
|  | Heating | Standard | A | 5.60
|  |  | Max | A | 11.00
|  |  | Min | A | 1.30
| Current | MCA |  | A | 13.10
|  | MFA |  | A | 15.00
Efficiency | Cooling | EER |  | W/W | 2.9
|  | SEER |  | W/W | 6
|  | SEER_Class |  | W/W | A+
| Heating | COP |  | W/W | 3.08
|  | SCOP |  | W/W | 4
|  | SCOP_Class |  | W/W | A+
Piping Connections | Liquid Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 9.52
| Gas Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 15.88
Wiring connections | Communication | Min. |  | ㎟ | 0.75
DVM Pro 2.0
Product Specification
System_RGNN_2a (Continued)
System
Wiring connections | Communication | Comm.Layer |  |  | F1, F2
Refrigerant | Type |  |  |  | R410A
| Factory Charging |  |  | kg | 2.90
Operating Temp. Range | Cooling | Min. |  | °C | -20.0
|  | Max. |  | °C | 50.0
| Heating | Min. |  | °C | -25.0
|  | Max. |  | °C | 24.0
DVM Pro 2.0
Product Specification
System_RGNN_2a (Continued)
Outdoor Unit
Model Name |  |  |  |  | AC100JXSCGH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 3 ¦ 4 ¦ 380-415 ¦ 50
Casing | Material | Body |  |  | EGI Steel Plate
|  | Base |  |  | EGI Steel Plate
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Compressor | Model Name |  |  |  | UG5T450FXAJX
| Quantity |  |  | EA | 1
| Type |  |  |  | Twin BLDC Inverter Rotary
| Output |  |  | kW | 4.01
| Oil | Type |  |  | POE
|  | Initial charge |  | cc | 1700
Fan | Type |  |  |  | Propeller
| Discharge direction |  |  |  | Horizontal
| Air Flow Rate | High |  | CMM | 112
Fan Motor | Type |  |  |  | BLDC
Sound | Sound Pressure Level | Cooling |  | dB(A) | 50
|  | Heating |  | dB(A) | 50
| Sound Power Level | Cooling |  | dB(A) | 66
External Dimension | Net Weight |  |  | kg | 96.00
| Shipping Weight |  |  | kg | 106.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_RGNN_2a (Continued)
Indoor Unit
Model Name |  |  |  |  | AC100MNTCEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
| Fin Treatment |  |  |  | Green Hydrophile
Fan | Type |  |  |  | Crossflow
| Air Flow Rate | High |  | CMM | 24
|  | Mid |  | CMM | 22
|  | Low |  | CMM | 19
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
| Output |  |  | W | 58
Sound | Sound Pressure Level | High |  | dB(A) | 0
|  | Mid |  | dB(A) | 49
|  | Low |  | dB(A) | 0
| Sound Power Level | Cooling |  | dB(A) | 65
External Dimension | Net Weight |  |  | kg | 18.50
| Shipping Weight |  |  | kg | 21.50
| Net Dimensions | W |  | mm | 1280
|  | H |  | mm | 253
|  | D |  | mm | 345
| Shipping Dimensions | W |  | mm | 1352
|  | H |  | mm | 326
|  | D |  | mm | 420
DVM Pro 2.0
Product Specification
System_UPS_3a
System
Model Name |  |  |  |  | AC071JXSCEH/EU+AC071KNADEH/EU
Mode |  |  |  |  | HP
Performance | kW |  |  |  | 7.1
| Capacity | Cooling | Standard | kW | 7.10
|  |  | Max | kW | 8.50
|  |  | Min | kW | 2.00
|  | Heating | Standard | kW | 8.00
|  |  | Max | kW | 10.00
|  |  | Min | kW | 3.00
Power | Power Input | Cooling | Standard | kW | 1.86
|  |  | Max | kW | 2.30
|  |  | Min | kW | 0.75
|  | Heating | Standard | kW | 2.33
|  |  | Max | kW | 5.10
|  |  | Min | kW | 0.56
| Current Input | Cooling | Standard | A | 8.40
|  |  | Max | A | 10.30
|  |  | Min | A | 4.10
|  | Heating | Standard | A | 10.60
|  |  | Max | A | 22.00
|  |  | Min | A | 3.00
| Current | MCA |  | A | 25.00
|  | MFA |  | A | 30.00
Efficiency | Cooling | EER |  | W/W | 3.81720430107527
|  | SEER |  | W/W | 6.5
|  | SEER_Class |  | W/W | A++
| Heating | COP |  | W/W | 3.43347639484979
|  | SCOP |  | W/W | 4
|  | SCOP_Class |  | W/W | A+
Piping Connections | Liquid Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 9.52
| Gas Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 15.88
Wiring connections | Communication | Min. |  | ㎟ | 0.75
DVM Pro 2.0
Product Specification
System_UPS_3a (Continued)
System
Wiring connections | Communication | Comm.Layer |  |  | F1, F2
Refrigerant | Type |  |  |  | R410A
| Factory Charging |  |  | kg | 2.90
Operating Temp. Range | Cooling | Min. |  | °C | -20.0
|  | Max. |  | °C | 50.0
| Heating | Min. |  | °C | -25.0
|  | Max. |  | °C | 24.0
DVM Pro 2.0
Product Specification
System_UPS_3a (Continued)
Outdoor Unit
Model Name |  |  |  |  | AC071JXSCEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Casing | Material | Body |  |  | EGI Steel Plate
|  | Base |  |  | EGI Steel Plate
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Compressor | Model Name |  |  |  | UG5T450FUEJX
| Quantity |  |  | EA | 1
| Type |  |  |  | Twin BLDC Inverter Rotary
| Output |  |  | kW | 4.12
| Oil | Type |  |  | POE
|  | Initial charge |  | cc | 1700
Fan | Type |  |  |  | Propeller
| Discharge direction |  |  |  | Horizontal
| Air Flow Rate | High |  | CMM | 112
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
Sound | Sound Pressure Level | Cooling |  | dB(A) | 49
|  | Heating |  | dB(A) | 49
| Sound Power Level | Cooling |  | dB(A) | 65
External Dimension | Net Weight |  |  | kg | 96.00
| Shipping Weight |  |  | kg | 106.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_UPS_3a (Continued)
Indoor Unit
Model Name |  |  |  |  | AC071KNADEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Fan | Type |  |  |  | Cross flow
| Air Flow Rate | High |  | CMM | 17
|  | Mid |  | CMM | 15
|  | Low |  | CMM | 13
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
| Output |  |  | W | 27
Sound | Sound Pressure Level | High |  | dB(A) | 43
|  | Mid |  | dB(A) | 40
|  | Low |  | dB(A) | 35
|  | Silent |  | dB(A) | 30
| Sound Power Level | Cooling |  | dB(A) | 61
External Dimension | Net Weight |  |  | kg | 14.50
| Shipping Weight |  |  | kg | 17.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_UPS_3b
System
Model Name |  |  |  |  | AC071JXSCEH/EU+AC071KNADEH/EU
Mode |  |  |  |  | HP
Performance | kW |  |  |  | 7.1
| Capacity | Cooling | Standard | kW | 7.10
|  |  | Max | kW | 8.50
|  |  | Min | kW | 2.00
|  | Heating | Standard | kW | 8.00
|  |  | Max | kW | 10.00
|  |  | Min | kW | 3.00
Power | Power Input | Cooling | Standard | kW | 1.86
|  |  | Max | kW | 2.30
|  |  | Min | kW | 0.75
|  | Heating | Standard | kW | 2.33
|  |  | Max | kW | 5.10
|  |  | Min | kW | 0.56
| Current Input | Cooling | Standard | A | 8.40
|  |  | Max | A | 10.30
|  |  | Min | A | 4.10
|  | Heating | Standard | A | 10.60
|  |  | Max | A | 22.00
|  |  | Min | A | 3.00
| Current | MCA |  | A | 25.00
|  | MFA |  | A | 30.00
Efficiency | Cooling | EER |  | W/W | 3.81720430107527
|  | SEER |  | W/W | 6.5
|  | SEER_Class |  | W/W | A++
| Heating | COP |  | W/W | 3.43347639484979
|  | SCOP |  | W/W | 4
|  | SCOP_Class |  | W/W | A+
Piping Connections | Liquid Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 9.52
| Gas Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 15.88
Wiring connections | Communication | Min. |  | ㎟ | 0.75
DVM Pro 2.0
Product Specification
System_UPS_3b (Continued)
System
Wiring connections | Communication | Comm.Layer |  |  | F1, F2
Refrigerant | Type |  |  |  | R410A
| Factory Charging |  |  | kg | 2.90
Operating Temp. Range | Cooling | Min. |  | °C | -20.0
|  | Max. |  | °C | 50.0
| Heating | Min. |  | °C | -25.0
|  | Max. |  | °C | 24.0
DVM Pro 2.0
Product Specification
System_UPS_3b (Continued)
Outdoor Unit
Model Name |  |  |  |  | AC071JXSCEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Casing | Material | Body |  |  | EGI Steel Plate
|  | Base |  |  | EGI Steel Plate
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Compressor | Model Name |  |  |  | UG5T450FUEJX
| Quantity |  |  | EA | 1
| Type |  |  |  | Twin BLDC Inverter Rotary
| Output |  |  | kW | 4.12
| Oil | Type |  |  | POE
|  | Initial charge |  | cc | 1700
Fan | Type |  |  |  | Propeller
| Discharge direction |  |  |  | Horizontal
| Air Flow Rate | High |  | CMM | 112
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
Sound | Sound Pressure Level | Cooling |  | dB(A) | 49
|  | Heating |  | dB(A) | 49
| Sound Power Level | Cooling |  | dB(A) | 65
External Dimension | Net Weight |  |  | kg | 96.00
| Shipping Weight |  |  | kg | 106.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_UPS_3b (Continued)
Indoor Unit
Model Name |  |  |  |  | AC071KNADEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Fan | Type |  |  |  | Cross flow
| Air Flow Rate | High |  | CMM | 17
|  | Mid |  | CMM | 15
|  | Low |  | CMM | 13
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
| Output |  |  | W | 27
Sound | Sound Pressure Level | High |  | dB(A) | 43
|  | Mid |  | dB(A) | 40
|  | Low |  | dB(A) | 35
|  | Silent |  | dB(A) | 30
| Sound Power Level | Cooling |  | dB(A) | 61
External Dimension | Net Weight |  |  | kg | 14.50
| Shipping Weight |  |  | kg | 17.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_PSP_4a
System
Model Name |  |  |  |  | AC071JXSCEH/EU+AC071KNADEH/EU
Mode |  |  |  |  | HP
Performance | kW |  |  |  | 7.1
| Capacity | Cooling | Standard | kW | 7.10
|  |  | Max | kW | 8.50
|  |  | Min | kW | 2.00
|  | Heating | Standard | kW | 8.00
|  |  | Max | kW | 10.00
|  |  | Min | kW | 3.00
Power | Power Input | Cooling | Standard | kW | 1.86
|  |  | Max | kW | 2.30
|  |  | Min | kW | 0.75
|  | Heating | Standard | kW | 2.33
|  |  | Max | kW | 5.10
|  |  | Min | kW | 0.56
| Current Input | Cooling | Standard | A | 8.40
|  |  | Max | A | 10.30
|  |  | Min | A | 4.10
|  | Heating | Standard | A | 10.60
|  |  | Max | A | 22.00
|  |  | Min | A | 3.00
| Current | MCA |  | A | 25.00
|  | MFA |  | A | 30.00
Efficiency | Cooling | EER |  | W/W | 3.81720430107527
|  | SEER |  | W/W | 6.5
|  | SEER_Class |  | W/W | A++
| Heating | COP |  | W/W | 3.43347639484979
|  | SCOP |  | W/W | 4
|  | SCOP_Class |  | W/W | A+
Piping Connections | Liquid Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 9.52
| Gas Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 15.88
Wiring connections | Communication | Min. |  | ㎟ | 0.75
DVM Pro 2.0
Product Specification
System_PSP_4a (Continued)
System
Wiring connections | Communication | Comm.Layer |  |  | F1, F2
Refrigerant | Type |  |  |  | R410A
| Factory Charging |  |  | kg | 2.90
Operating Temp. Range | Cooling | Min. |  | °C | -20.0
|  | Max. |  | °C | 50.0
| Heating | Min. |  | °C | -25.0
|  | Max. |  | °C | 24.0
DVM Pro 2.0
Product Specification
System_PSP_4a (Continued)
Outdoor Unit
Model Name |  |  |  |  | AC071JXSCEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Casing | Material | Body |  |  | EGI Steel Plate
|  | Base |  |  | EGI Steel Plate
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Compressor | Model Name |  |  |  | UG5T450FUEJX
| Quantity |  |  | EA | 1
| Type |  |  |  | Twin BLDC Inverter Rotary
| Output |  |  | kW | 4.12
| Oil | Type |  |  | POE
|  | Initial charge |  | cc | 1700
Fan | Type |  |  |  | Propeller
| Discharge direction |  |  |  | Horizontal
| Air Flow Rate | High |  | CMM | 112
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
Sound | Sound Pressure Level | Cooling |  | dB(A) | 49
|  | Heating |  | dB(A) | 49
| Sound Power Level | Cooling |  | dB(A) | 65
External Dimension | Net Weight |  |  | kg | 96.00
| Shipping Weight |  |  | kg | 106.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_PSP_4a (Continued)
Indoor Unit
Model Name |  |  |  |  | AC071KNADEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Fan | Type |  |  |  | Cross flow
| Air Flow Rate | High |  | CMM | 17
|  | Mid |  | CMM | 15
|  | Low |  | CMM | 13
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
| Output |  |  | W | 27
Sound | Sound Pressure Level | High |  | dB(A) | 43
|  | Mid |  | dB(A) | 40
|  | Low |  | dB(A) | 35
|  | Silent |  | dB(A) | 30
| Sound Power Level | Cooling |  | dB(A) | 61
External Dimension | Net Weight |  |  | kg | 14.50
| Shipping Weight |  |  | kg | 17.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_PSP_4b
System
Model Name |  |  |  |  | AC071JXSCEH/EU+AC071KNADEH/EU
Mode |  |  |  |  | HP
Performance | kW |  |  |  | 7.1
| Capacity | Cooling | Standard | kW | 7.10
|  |  | Max | kW | 8.50
|  |  | Min | kW | 2.00
|  | Heating | Standard | kW | 8.00
|  |  | Max | kW | 10.00
|  |  | Min | kW | 3.00
Power | Power Input | Cooling | Standard | kW | 1.86
|  |  | Max | kW | 2.30
|  |  | Min | kW | 0.75
|  | Heating | Standard | kW | 2.33
|  |  | Max | kW | 5.10
|  |  | Min | kW | 0.56
| Current Input | Cooling | Standard | A | 8.40
|  |  | Max | A | 10.30
|  |  | Min | A | 4.10
|  | Heating | Standard | A | 10.60
|  |  | Max | A | 22.00
|  |  | Min | A | 3.00
| Current | MCA |  | A | 25.00
|  | MFA |  | A | 30.00
Efficiency | Cooling | EER |  | W/W | 3.81720430107527
|  | SEER |  | W/W | 6.5
|  | SEER_Class |  | W/W | A++
| Heating | COP |  | W/W | 3.43347639484979
|  | SCOP |  | W/W | 4
|  | SCOP_Class |  | W/W | A+
Piping Connections | Liquid Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 9.52
| Gas Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 15.88
Wiring connections | Communication | Min. |  | ㎟ | 0.75
DVM Pro 2.0
Product Specification
System_PSP_4b (Continued)
System
Wiring connections | Communication | Comm.Layer |  |  | F1, F2
Refrigerant | Type |  |  |  | R410A
| Factory Charging |  |  | kg | 2.90
Operating Temp. Range | Cooling | Min. |  | °C | -20.0
|  | Max. |  | °C | 50.0
| Heating | Min. |  | °C | -25.0
|  | Max. |  | °C | 24.0
DVM Pro 2.0
Product Specification
System_PSP_4b (Continued)
Outdoor Unit
Model Name |  |  |  |  | AC071JXSCEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Casing | Material | Body |  |  | EGI Steel Plate
|  | Base |  |  | EGI Steel Plate
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Compressor | Model Name |  |  |  | UG5T450FUEJX
| Quantity |  |  | EA | 1
| Type |  |  |  | Twin BLDC Inverter Rotary
| Output |  |  | kW | 4.12
| Oil | Type |  |  | POE
|  | Initial charge |  | cc | 1700
Fan | Type |  |  |  | Propeller
| Discharge direction |  |  |  | Horizontal
| Air Flow Rate | High |  | CMM | 112
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
Sound | Sound Pressure Level | Cooling |  | dB(A) | 49
|  | Heating |  | dB(A) | 49
| Sound Power Level | Cooling |  | dB(A) | 65
External Dimension | Net Weight |  |  | kg | 96.00
| Shipping Weight |  |  | kg | 106.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_PSP_4b (Continued)
Indoor Unit
Model Name |  |  |  |  | AC071KNADEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Fan | Type |  |  |  | Cross flow
| Air Flow Rate | High |  | CMM | 17
|  | Mid |  | CMM | 15
|  | Low |  | CMM | 13
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
| Output |  |  | W | 27
Sound | Sound Pressure Level | High |  | dB(A) | 43
|  | Mid |  | dB(A) | 40
|  | Low |  | dB(A) | 35
|  | Silent |  | dB(A) | 30
| Sound Power Level | Cooling |  | dB(A) | 61
External Dimension | Net Weight |  |  | kg | 14.50
| Shipping Weight |  |  | kg | 17.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_SERW_5a
System
Model Name |  |  |  |  | AC071JXSCEH/EU+AC071KNADEH/EU
Mode |  |  |  |  | HP
Performance | kW |  |  |  | 7.1
| Capacity | Cooling | Standard | kW | 7.10
|  |  | Max | kW | 8.50
|  |  | Min | kW | 2.00
|  | Heating | Standard | kW | 8.00
|  |  | Max | kW | 10.00
|  |  | Min | kW | 3.00
Power | Power Input | Cooling | Standard | kW | 1.86
|  |  | Max | kW | 2.30
|  |  | Min | kW | 0.75
|  | Heating | Standard | kW | 2.33
|  |  | Max | kW | 5.10
|  |  | Min | kW | 0.56
| Current Input | Cooling | Standard | A | 8.40
|  |  | Max | A | 10.30
|  |  | Min | A | 4.10
|  | Heating | Standard | A | 10.60
|  |  | Max | A | 22.00
|  |  | Min | A | 3.00
| Current | MCA |  | A | 25.00
|  | MFA |  | A | 30.00
Efficiency | Cooling | EER |  | W/W | 3.81720430107527
|  | SEER |  | W/W | 6.5
|  | SEER_Class |  | W/W | A++
| Heating | COP |  | W/W | 3.43347639484979
|  | SCOP |  | W/W | 4
|  | SCOP_Class |  | W/W | A+
Piping Connections | Liquid Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 9.52
| Gas Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 15.88
Wiring connections | Communication | Min. |  | ㎟ | 0.75
DVM Pro 2.0
Product Specification
System_SERW_5a (Continued)
System
Wiring connections | Communication | Comm.Layer |  |  | F1, F2
Refrigerant | Type |  |  |  | R410A
| Factory Charging |  |  | kg | 2.90
Operating Temp. Range | Cooling | Min. |  | °C | -20.0
|  | Max. |  | °C | 50.0
| Heating | Min. |  | °C | -25.0
|  | Max. |  | °C | 24.0
DVM Pro 2.0
Product Specification
System_SERW_5a (Continued)
Outdoor Unit
Model Name |  |  |  |  | AC071JXSCEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Casing | Material | Body |  |  | EGI Steel Plate
|  | Base |  |  | EGI Steel Plate
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Compressor | Model Name |  |  |  | UG5T450FUEJX
| Quantity |  |  | EA | 1
| Type |  |  |  | Twin BLDC Inverter Rotary
| Output |  |  | kW | 4.12
| Oil | Type |  |  | POE
|  | Initial charge |  | cc | 1700
Fan | Type |  |  |  | Propeller
| Discharge direction |  |  |  | Horizontal
| Air Flow Rate | High |  | CMM | 112
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
Sound | Sound Pressure Level | Cooling |  | dB(A) | 49
|  | Heating |  | dB(A) | 49
| Sound Power Level | Cooling |  | dB(A) | 65
External Dimension | Net Weight |  |  | kg | 96.00
| Shipping Weight |  |  | kg | 106.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_SERW_5a (Continued)
Indoor Unit
Model Name |  |  |  |  | AC071KNADEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Fan | Type |  |  |  | Cross flow
| Air Flow Rate | High |  | CMM | 17
|  | Mid |  | CMM | 15
|  | Low |  | CMM | 13
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
| Output |  |  | W | 27
Sound | Sound Pressure Level | High |  | dB(A) | 43
|  | Mid |  | dB(A) | 40
|  | Low |  | dB(A) | 35
|  | Silent |  | dB(A) | 30
| Sound Power Level | Cooling |  | dB(A) | 61
External Dimension | Net Weight |  |  | kg | 14.50
| Shipping Weight |  |  | kg | 17.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_SERW_5b
System
Model Name |  |  |  |  | AC071JXSCEH/EU+AC071KNADEH/EU
Mode |  |  |  |  | HP
Performance | kW |  |  |  | 7.1
| Capacity | Cooling | Standard | kW | 7.10
|  |  | Max | kW | 8.50
|  |  | Min | kW | 2.00
|  | Heating | Standard | kW | 8.00
|  |  | Max | kW | 10.00
|  |  | Min | kW | 3.00
Power | Power Input | Cooling | Standard | kW | 1.86
|  |  | Max | kW | 2.30
|  |  | Min | kW | 0.75
|  | Heating | Standard | kW | 2.33
|  |  | Max | kW | 5.10
|  |  | Min | kW | 0.56
| Current Input | Cooling | Standard | A | 8.40
|  |  | Max | A | 10.30
|  |  | Min | A | 4.10
|  | Heating | Standard | A | 10.60
|  |  | Max | A | 22.00
|  |  | Min | A | 3.00
| Current | MCA |  | A | 25.00
|  | MFA |  | A | 30.00
Efficiency | Cooling | EER |  | W/W | 3.81720430107527
|  | SEER |  | W/W | 6.5
|  | SEER_Class |  | W/W | A++
| Heating | COP |  | W/W | 3.43347639484979
|  | SCOP |  | W/W | 4
|  | SCOP_Class |  | W/W | A+
Piping Connections | Liquid Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 9.52
| Gas Pipe | Type |  |  | Flaring
|  | Diameter |  | mm | 15.88
Wiring connections | Communication | Min. |  | ㎟ | 0.75
DVM Pro 2.0
Product Specification
System_SERW_5b (Continued)
System
Wiring connections | Communication | Comm.Layer |  |  | F1, F2
Refrigerant | Type |  |  |  | R410A
| Factory Charging |  |  | kg | 2.90
Operating Temp. Range | Cooling | Min. |  | °C | -20.0
|  | Max. |  | °C | 50.0
| Heating | Min. |  | °C | -25.0
|  | Max. |  | °C | 24.0
DVM Pro 2.0
Product Specification
System_SERW_5b (Continued)
Outdoor Unit
Model Name |  |  |  |  | AC071JXSCEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Casing | Material | Body |  |  | EGI Steel Plate
|  | Base |  |  | EGI Steel Plate
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Compressor | Model Name |  |  |  | UG5T450FUEJX
| Quantity |  |  | EA | 1
| Type |  |  |  | Twin BLDC Inverter Rotary
| Output |  |  | kW | 4.12
| Oil | Type |  |  | POE
|  | Initial charge |  | cc | 1700
Fan | Type |  |  |  | Propeller
| Discharge direction |  |  |  | Horizontal
| Air Flow Rate | High |  | CMM | 112
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
Sound | Sound Pressure Level | Cooling |  | dB(A) | 49
|  | Heating |  | dB(A) | 49
| Sound Power Level | Cooling |  | dB(A) | 65
External Dimension | Net Weight |  |  | kg | 96.00
| Shipping Weight |  |  | kg | 106.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426
DVM Pro 2.0
Product Specification
System_SERW_5b (Continued)
Indoor Unit
Model Name |  |  |  |  | AC071KNADEH/EU
Power Supply |  |  |  | Ø, #, V, Hz | 1 ¦ 2 ¦ 220-240 ¦ 50
Heat Exchanger | Type |  |  |  | Fin & Tube
| Material | Fin |  |  | Al
|  | Tube |  |  | Cu
Fan | Type |  |  |  | Cross flow
| Air Flow Rate | High |  | CMM | 17
|  | Mid |  | CMM | 15
|  | Low |  | CMM | 13
Fan Motor | Type |  |  |  | BLDC
| Quantity |  |  | EA | 1
| Output |  |  | W | 27
Sound | Sound Pressure Level | High |  | dB(A) | 43
|  | Mid |  | dB(A) | 40
|  | Low |  | dB(A) | 35
|  | Silent |  | dB(A) | 30
| Sound Power Level | Cooling |  | dB(A) | 61
External Dimension | Net Weight |  |  | kg | 14.50
| Shipping Weight |  |  | kg | 17.00
| Net Dimensions | W |  | mm | 940
|  | H |  | mm | 1420
|  | D |  | mm | 330
| Shipping Dimensions | W |  | mm | 995
|  | H |  | mm | 1598
|  | D |  | mm | 426